## Triple Splits
(Up to 2 x Triple-Split split systems)
Site/Store Name | TBC
Site Address | TBC
Commissioning Date | TBC
Installation company | TBC
Address | TBC
Telephone | TBC
e-mail | TBC
Commissioning Engineer | TBC
Certificate Number | TBC
Local Controller Model | TBC
Local Controller location | TBC
Sub controller model and location | TBC
Central Controller Model | TBC
Weekly Timer model | TBC
Time switch settings | TBC
Network cable (used with Central Controller) | TBC
Room sensor used? Location? | Yes / No
Configured for auto restart? | TBC
Configured for controller temp. sensor? | TBC
Indoor number | 1 | 2 | 3 | 1 | 2 | 3
Indoor unit make/model details | TBC | TBC | TBC | TBC | TBC | TBC
Indoor serial number | TBC | TBC | TBC | TBC | TBC | TBC
Indoor location or reference | TBC | TBC | TBC | TBC | TBC | TBC
Outdoor unit make/model details | TBC |  |  | TBC
Outdoor serial number | TBC |  |  | TBC
Outdoor location or reference | TBC |  |  | TBC
Distribution board reference | TBC |  |  | TBC
Fuse size and type | TBC |  |  | TBC
Network address set from….. | TBC |  |  | TBC
Support and insulation effective? | Yes No |  |  | Yes No
Condensate removal ok? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
External pump fitted? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Protocol converter fitted? | Yes No | Yes No | Yes No | Yes No | Yes No | Yes No
Outdoor unit energised for 12 hours? | Yes No |  |  | Yes No
Refrigeration circuit
Strength tested under F-gas legislation? | Yes No |  |  | Yes No
Leak tested under F-gas legislation? | Yes No |  |  | Yes No
Vacuum achieved? | TBC |  |  | TBC
Maintained for 30 minutes? | Yes No |  |  | Yes No
Refrigerant
Refrigerant type | TBC |  |  | TBC
Pipe Sizes (Main) | TBC |  |  | TBC
Pipe Sizes (Branch) | TBC | TBC | TBC | TBC | TBC | TBC
refrigerant circuit length - main pipes | TBC |  |  | TBC
Refrigerant circuit length - branch pipes | TBC | TBC | TBC | TBC | TBC | TBC
Additional refrigerant added | 0 |  |  | 0
Factory refrigerant charge (kg) | 0 |  |  | 0
Total system refrigerant charge (kg) | 0 |  |  | 0
Running tests (C/H) @ test condition | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat | Cool / Heat
02 return air temperature | Required | Required | Required | Required | Required | Required
03 indoor coil - liquid temperature | Required | Required | Required | Required | Required | Required
04 indoor coil - vapour temperature | Required | Required | Required | Required | Required | Required
60 outdoor coil - liquid temperature | Required |  |  | Required
61 ambient temperature | Required |  |  | Required
62 compressor discharge temperature | Required |  |  | Required
63 compressor suction temperature | Required |  |  | Required
supply air temperature (HEAT & COOL) | Required | Required | Required | Required | Required | Required
Voltage across terminals L-N | Required |  |  | Required
Running current | Required |  |  | Required
Configurable items
03 network address | TBC |  |  | TBC
12 outdoor number | Required |  |  | Required
13 indoor unit number | Required | Required | Required | Required | Required | Required
14 indoor unit role | Required | Required | Required | Required | Required | Required
19 louver functions | Required | Required | Required | Required | Required | Required
5d air flow correction | Required | Required | Required | Required | Required | Required
Comments
Note on B4: Enter full site/store name
Note on B5: Enter full site address
Note on B18: Each day may be programmed separately, with up to 3 operating periods per day - if using scheduled timer
Note on B19: The network cable should be terminated in the indoor unit with Protocol Converter fitted. The screen shall be continuous and earthed at a single point. Minimum 1.5mm² up to 500m, 2.0mm² over 500m If a Protocol Converter has not been fitted, the cable should be left with enough slack for future use.
Note on B20: A single room sensor can be added to the group wiring and will provide the temperature value for the entire group. Configuration item 32 must remain at 0000
Note on B21: To enable group auto-restart, configuration item 28 to 0001.
Note on B22: Provides operating temperature value for the entire group. Configuration item 32 must be set to 0001. If the temperature sensor is enabled, the controller must be located in a representative position.
Note on B31: Suggested breaker sizes: SM56* - 16A SM80* - 16A SM110* - 20A SM140* - 25A SM160* - 32A SM2244 - 16A SM2804 - 20A SP40* - 10A SP56* - 16A SP80* - 16A SP110* - 16A SP140* - 25A SP110*AT8 - 10A SP140*AT8 - 16A SP160*AT8 - 16A
Note on B32: if applicable
Note on B33: Both liquid and vapour lines require full insulation (0 or 1 class).
Note on B34: Check that condensate is drained effectively. Circle PUMP if an external lift pump is used.
Note on B36: Only necessary for network control. A group will only have only one protocol converter fitted within the HEADER indoor unit.
Note on B37: Mains voltage should be supplied to the outdoor unit as soon as practical to warm the compressor.
Note on B39: Pressure should be increased in 3 stages - to ensure that the leak test may be conducted safely. Strength tested to not less than 1.3 x M.W.P
Note on B40: No maximum time for the leak test but there will be no drop in pressure during a successful test. Leak tested to 1.0 - 1.1 x M.W.P
Note on B41: The vacuum required will be dependant on the average temperature of the system (halfway between indoor and outdoor temperatures) A minimum of 4 Torr (530 Pa) should be achieved in all cases however, If the average temperature is below 10ºC a vacuum of 2 Torr (400 Pa) must be achieved. 5ºC requires a vacuum of a least 3 Torr (260 Pa) When below freezing point, the system cannot be reliably dehydrated
Note on B45: When systems are installed on 'existing' R22/R407c pipe work and the suction pipe is one step larger than standard, follow the 'Existing Pipe' instructions found within installation manual.
Note on B47: The linear (actual) length of the refrigeration pipe work between the outdoor unit and the 'Distributor' Note RAV-SM1603AT-E Max total pipe run is 50m (main + longest branch) Max length of a single branch must not exceed 15m, subtractive difference between branch lengths must not exceed 10m. RAV-SM2244-2804AT-E Max total pipe run is 70m (main + longest branch) irrespective of outdoor unit model Max length of a single branch must not exceed 20m, subtractive difference between branch lengths must not exceed 10m.
Note on C47: L1 - From condenser to distributor
Note on F47: L1 - From condenser to distributor
Note on B48: The total linear (actual) length of the refrigeration circuit - from Distributor to each indoor unit. Note RAV-SM1603AT-E Max total pipe run is 50m (main + longest branch) Max length of a single branch must not exceed 15m, subtractive difference between branch lengths must not exceed 10m. RAV-SM2244-2804AT-E Max total pipe run is 70m (main + longest branch) irrespective of outdoor unit model Max length of a single branch must not exceed 20m, subtractive difference between branch lengths must not exceed 10m.
Note on C48: L2 - From distributor to indoor
Note on D48: L3 - From distributor to indoor
Note on E48: L4 - From distributor to indoor
Note on F48: L2 - From distributor to indoor
Note on G48: L3 - From distributor to indoor
Note on H48: L4 - From distributor to indoor
Note on B49: The calculation's are DI For 1603AT outdoor units with 3 x 56* indoors (L1) Main Pipe minus 28m x 0.04kg/m = + (L2) Branch 1 minus 2m x 0.02kg/m = + (L3) Branch 2 minus 2m x 0.02kg/m = + (L4) Branch 3 minus 2m x 0.02kg/m = Additional charge =________ kg DI Big For 2244-2804AT outdoor units with 3 x 110*-140* indoors (L1) Main Pipe minus 28m x 0.08kg/m = + (L2) Branch 1 minus 2m x 0.04kg/m = + (L3) Branch 2 minus 2m x 0.04kg/m = + (L4) Branch 3 minus 2m x 0.04kg/m = Additional charge =________ kg Note DI/SDI range Min pipe run is 5m total Max run is 50m total irrespective of outdoor unit (L1 + L2 or L1 + L3 or L1 + L4) DI Big Range Min pipe run 7.5m total Max run is 70m total (L1 + L2 or L1 + L3 or L1 + L4) Always refer to the 'twin-kit' or installation manual
Note on B50: Factory refrigerant charge can be found on the name plate of the outdoor unit.
Note on B51: Total system charge is the additional charge plus the factory charge.
Note on B52: To initiate Press CHECK(Test) for 4 seconds. When the controller displays TEST, use mode to select heat or cool and use UNIT to choose the system to be tested. Note - systems MUST be tested individually. Values for both heating and cooling operations should be shown. This does not provide a 100% demand. To check values during test, (after compressor operation has started), press CHECK(Test)+CLEAR(CL). Press CHECK(Test) to terminate the test.
Note on B60: The temperature (DB) of the air supplied during the cooling and heating processes. Also known as air outlet temperature.
Note on B61: This measurement should be taken while the compressor is running.
Note on B62: Input current is limited by the inverter.
Note on B63: To access: Press CHECK(Test) & SET & CL buttons for 4 seconds
Note on B64: Only necessary when network control is used. Factory default 0099 May be set from the remote controller, through configuration item 03.
Note on B65: Automatically addressed though may be changed to reflect site reference.
Note on B66: Automatic addressing - generally 0001 unless twinned indoor units are used.
Note on B67: Individual system = 0000 Control group Header = 0001 (only 1 lead unit within a group) Follower = 0002 (up to a maximum of 7 followers)